## Sheet1
Initial condition | Tested functions | Actions | Results | Comments
The air compressor system is in it's initial state: 1. The PC-100 is shut down 2. The OFF status is indicated by the OI-100.2 led 3. Emergency and maintenance are not active. 4. Other leds status: - OI-100.3 is OFF - OI-100.4 is OFF - OI-100.5 is ON - OI-100.6 is OFF - OI-100.7 is OFF | Turning on the air compressor system | The system is started by an operator pressing the H-100.1 button. | The PC-100 air compressor system is started, indicated by OI-100.1 led. The OI-100.2 led is OFF. The pressure increases until it reaches 10 bar.
| Turning off the air compressor system | The system is stopped by an operator pressing the H-100.2 button | The PC-100 air compressor system is stopped, indicated by OI-100.2 led. The OI-100.1 led is OFF. The tank pressure remains the same.
| Emergency stop | Emergency stop can be triggered by the H-100.3 button, or by the system automatically when reaching the maximum pressure of 10.5 bar | The tank starts emptying until the emergency reset button is pressed (H-100.4). This is indicated by OI-100.4 led. The OI-100.3 led flashes at 1 Hz. The PID is turned OFF, status indicated by OI-100.2 led. The PID cannot be turned on until the emergency reset button is pressed(H-100.4). If the tank pressure reaches 0 bar then OI-100.6 led is turned ON.
| Emergency in case of high pressure | This type of emergency is triggered when tank pressure is between 10.2 and 10.5 bar. | OI-100.7 led flashes at 5Hz rate.
| Maintenance | The maintenance is started by pressing the H-100.5 button. | Tank starts emptying at a low rate, this is indicated by OI-100.4 led. If the tank pressure reaches 0 bar then the OI-100.6 led turns ON. Maintenance is stopped by pressing the maintenance reset button (H-100.6). During maintenance the PID is stopped, this is indicated by the OI-100.2 led, and cannot by turned on until the maintenance reset button is pressed.
| Brush | The brush is activated by pressing the Brush state button | The tank starts emptying at a low rate. The PID is still turned on, the status is indicated by the OI-100.1 led. The status of the brush is indicated by OI-100.5 led (OFF).
All functions are approved
Note on E2: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK
Note on E3: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK
Note on E4: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK
Note on E5: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK
Note on E6: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK
Note on E7: [Kommenttiketju] Excel-versiosi avulla voit lukea tämän kommenttiketjun, mutta siihen tehdyt muutokset poistetaan, jos tiedosto avataan uudemmassa Excel-versiossa. Lisätietoja: https://go.microsoft.com/fwlink/?linkid=870924 Kommentti: OK